Copyright 2021 AIA
MasterSpec Full Length
(PM Update 05/23)

PRODUCT MASTERSPEC LICENSED BY DELTEK, LLC TO MURDOCK MANUFACTURING; MORRIS GROUP INTERNATIONAL.


Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Murdock Manufacturing; Morris Group International ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.
For more information, contact Murdock Manufacturing; Morris Group International, 15125 Proctor Avenue, City of Industry, CA 91746; Phone: (626) 333-2543 | (800) 591-9081; Fax: <Insert Fax number>; Website: www.murdockmfg.com; Email: dyoung@acorneng.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit Deltek.com

 HYPERLINK "http://" .

SECTION 224716 - PRESSURE WATER COOLERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>
Revise this Section by deleting and inserting text to meet Project-specific requirements.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes pressure water coolers and related components.

1.2 ACTION SUBMITTALS
Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.
A. Product Data: For each type of pressure water cooler.

1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

2. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.
Retain "Sustainable Design Submittals" Paragraph below if required to attain sustainability rating or to track sustainability submittals.
B. Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED (including v4), IgCC, ASHRAE 189.1, and Green Globes for fixtures and equipment that consume water.

1. Product Data: For water consumption.
C. Shop Drawings: Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Maintenance Data: For pressure water coolers to include in maintenance manuals.

1.4 MAINTENANCE MATERIAL SUBMITTALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Filter Cartridges: Equal to <Insert number> percent of quantity installed for each type and size indicated, but no fewer than <Insert number> of each.

PART 2 -  PRODUCTS
Manufacturer and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contactor’s product selection, see section 016000 “Product Requirements.”

Product options commonly available from manufactures are included in square brackets throughout the Section Text. For definitions of terms and requirements for Contractor’s product selection, see Section 016000 “Product Requirements.”
2.1 PRESSURE WATER COOLERS

Copy "Pressure Water Coolers" Paragraph below and re-edit for each type of pressure water cooler required. 

Insert number to complete drawing designation. Use these designations on the Drawings to identify each pressure water cooler. 
A. Pressure Water Coolers <Insert drawing designation>: [Freestanding] [Flush to wall].
Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed. 
Provide A511.5 Series for compact freestanding water cooler applications.

Provide A611.8 Series for freestanding water cooler applications.

1. Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A511.5] [A611.8] or comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Oasis International.

c. <Insert manufacturer's name>.

2. Standards:

a. Comply with:
1) ASHRAE 15, or where applicable, ASHRAE 34.

2) ASME A112.18.1/CSA B125.

3) IAPMO IGC 226.

4) NSF 61 and NSF 372.

5) UL 399 and CSA C22.2, No. 120.

6) Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC).

3. Cabinet:

a. Finish: [All stainless steel] [Powder coated, with manufacturer's color selected from manufacturer's standard offerings], and stainless steel top.

In "Orientation" Subparagraph below, retain first or second option for floor-mounted units.

b. Orientation: [Positioned against wall] [Freestanding with enclosed back panel].

4. Bubbler: One [flexible bubbler with gray finish] [stainless steel bubbler], with adjustable stream regulator, located on each cabinet deck.
5. Control: [Push button] [Foot pedal].
6. Drain: Grid with 1-1/4 O.D. (32 mm) tailpiece.

7. Supply: NPS 3/8 (DN 10) with shutoff valve.

8. Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filtration" Subparagraph below only if required.

9. Filtration: Provide lead, chlorine, and cyst reduction filter rated for 1500 gal (6800 L) effective lifespan.

10. Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

b. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

11. Capacities and Characteristics:

In "Capacity" Subparagraph below, retain first option when Murdock A511.5 is selected.

a. Capacity: [5 gph (22.7 L/h)] [8 gph (36.44 L/h)] <Insert value>.

b. Ambient-Air Temperature: 90 deg F (32 deg C).

c. Inlet-Water Temperature: 80 deg F (27 deg C).

d. Cooled-Water Temperature: 50 deg F (10 deg C).

e. Electrical Characteristics:

1) Motor Horsepower: 1/5 HP (3.7 kW).

2) Volts: 120 V ac.

3) Phase: Single.

4) Hertz: 60.

In "Full-Load Amperes" Subparagraph below, retain first option when Murdock A511.5 is selected.

5) Full-Load Amperes: [3.6 A] [4.4 A]. <Insert value>.

f. Refrigerant: R-134a.

g. Insulate cooled water lines.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements.

12. Accessories:

a. Glass Filler: Deck mounted.

b. Hot Water Cup Filler: Deck mounted.

Copy "Pressure Water Coolers" Paragraph below and re-edit for each type of wall-mounted pressure water cooler required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each pressure water cooler.

B. Pressure Water Coolers <Insert drawing designation>: Wall mounted, stainless steel [, bi-level] [, bottle filler] [, vandal resistant] [, wheelchair accessible].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

A171.8-UG Series, barrier-free, wall-mounted water cooler.

A171.8-UG-BF Series, barrier-free, wall-mounted water cooler with push-button or sensor-operated bottle filler.

A171.8-UG-SO Series, barrier free, sensor operated, wall mounted.

A171.8-UG-SO-BF Series, barrier-free, sensor-operated, wall-mounted, electric water cooler push-button or sensor-operated bottle filler.

A171.8-UG-SOC Series, concealed sensor-operated, barrier-free, wall-mounted cooler.

A171.8-UG-SOC-BF Series, concealed sensor-operated, barrier-free, wall-mounted, electric water cooler with sensor-operated bottle filler.

A171.8-UG-VR Series, barrier-free, vandal-resistant button, wall-mounted water cooler.

A171.8-UG-VR-BF Series, barrier-free, vandal-resistant button, wall-mounted water cooler with push-button or sensor-operated bottle filler.

A171.8-UG-VR-D1-BFS Series, barrier-free, vandal-resistant, wall-mounted water cooler with vandal-resistant, push-button or sensor-operated bottle filler.

A172.8-UG Series, barrier-free, universal bi-level, wall-mounted water cooler.

A172.8-UG-BF Series, barrier-free, universal bi-level, wall-mounted water cooler with push-button or sensor-operated bottle filler.

A172.8-UG-SO Series, barrier-free, sensor-operated, bi-level wall-mounted water cooler.

A172.8-UG-SO-BF Series, sensor-operated, barrier-free, wall-mounted universal bi-level water cooler.

A172.8-UG-SOC Series, concealed sensor-operated, barrier-free, wall-mounted universal bi-level water cooler.

A172.8-UG-SOC-BF Series, concealed sensor-operated, barrier-free, wall-mounted universal bi-level water cooler with bottle filler.
A172.8-UG-VR Series, barrier-free, vandal-resistant button, universal bi-level, wall-mounted water cooler.

A172.8-UG-VR-BF Series, barrier-free, vandal resistant button, wall mounted bi-level electric water cooler with push-button or sensor-operated bottle filler.

A172.8-UG-VR-D1-BFS Series, barrier-free, vandal-resistant, universal bi-level, wall-mounted water cooler with vandal-resistant push-button or sensor-operated bottle filler.

A191.8 Series, barrier-free, wall-mounted chilled drinking fountain.

A191.8-BF Series, barrier-free, wall-mounted chilled drinking fountain with bottle filler and trim panel.

A192.8 Series, barrier-free, bi-level, wall-mounted chilled drinking fountain with 42-inch trim panel.

A192.8-BF Series, barrier-free, bi-level, wall-mounted chilled drinking fountain with bottle filler and 42‑inch trim panel.

A311.8 Series, wall-mounted water cooler.

A171408S-FG-VR Series, barrier-free, 14 gauge stainless steel, enhanced vandal resistance, wall-mounted water cooler.

A171408S-FG-VR-BFS Series, barrier-free, 14 gauge stainless steel, enhanced vandal resistance, wall-mounted water cooler with bottle filler.

A172408S-FG-VR-BFS Series, barrier-free, 14 gauge stainless steel, enhanced vandal resistance, bi-level, wall-mounted water cooler with bottle filler.

1. Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A171.8-UG] [A171.8-UG-BF] [A171.8-UG-SO] [A171.8-UG-SO-BF] [A171.8-UG-SOC] [A171.8-UG-SOC-BF] [A171.8-UG-VR] [A171.8-UG-VR-BF] [A171.8-UG-VR-D1-BFS] [A172.8-UG] [A172.8-UG-BF] [A172.8-UG-SO] [A172.8-UG-SO-BF] [A172.8-UG-SOC] [A172.8-UG-SOC-BF] [A172.8-UG-VR] [A172.8-UG-VR-BF] [A172.8-UG-VR-D1-BFS] [A191.8] [A191.8-BF] [A192.8] [A192.8-BF] [A311.8] [A171408S-FG-VR] [A171408S-FG-VR-BFS] [A172408S-FG-VR-BFS] or comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Oasis International.

c. <Insert manufacturer's name>.

2. Standards:

a. Comply with:

1) ASHRAE 15, or where applicable, ASHRAE 34.

2) ASME A112.18.1/CSA B125.

3) IAPMO IGC 226.

Retain first subparagraph below for wheelchair-accessible, wall-mounted, pressure water cooler.

4) ICC A117.1.

5) NSF 61 and NSF 372.

6) UL 399 and CSA C22.2, No. 120.

7) Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC).
3. Receptor: Type 304 stainless steel, No. 4, satin finish.

4. Bubbler: [One] [Two], [flexible with gray finish] [lead-free stainless steel], with anti-rotation, non-squirt design.

5. Maximum Water Flow: 0.5 gpm (1.9 L/m).

6. Cabinet: [Single] [Bi-level cabinets] [Bi-level cabinets with bi‑level skirt kit].

7. Control, Push Button: Push-button operated cartridge-style valve, having front access adjustable stream regulator.

Retain "Control, Vandal Resistant" Subparagraph below for models A171.8-UG-VR, A172.8-UG-VR, A171408S-FG-VR, A172408S-FG-VR, A171.8-UG-VR-BF, A172.8-UG-VR-BF, A171-FG-VR-BFS, A172-FG-VR-BFS, A171.8-UG-VR-D1-BFS, A172.8-UG-VR-D1-BFS, A191.8, A191.8-BF, A192.8, and A192.8-BF.

8. Control, Vandal Resistant: Round vandal-resistant push button, having front access adjustable stream regulator.
Retain "Control, Sensor Operated" Subparagraph below for models A171.8-UG-SO, A172.8-UG-SO, A171.8-UG-SO-BF, A172.8-UG-SO-BF, with front apron sensor and models A171.8-UG-SOC, A172.8-UG-SOC, A171.8-UG-SOC-BF, and A172.8-UG-SOC-BF with undermount sensor.

9. Control, Sensor Operated: Infrared sensor-operated valve, preset for maximum 20-second run time.

a. Sensor Location: [Front apron] [Undermount concealed].

b. Flow Restrictor: 0.5 gpm (1.9 L/m).

10. Valve: 9 V dc electronic solenoid valve.

Retain "Bottle Filler, Accessible" or "Bottle Filler, Vandal Resistant" Subparagraph below when a Bottle Filler is required.

Retain "Bottle Filler, Accessible" Subparagraph for models A171.8-UG-BF, A172.8-UG-BF, A171.8-UG-VR-BF, A172.8-UG-VR-BF, A191.8, A191.8-BF, A192.8, and A192.8-BF.

11. Bottle Filler, Accessible: Accessible contour design for coordinated installation with single station drinking fountain and bi-level accessible station. Drinking fountain basin will serve as drain.

a. Housing: Minimum 20-gauge, Type 304 stainless steel with exposed surfaces polished to No. 4 satin finish, with contour that aligns with drinking fountain basin. Fabricate bottle filler area from antimicrobial, impact-resistant ABS plastic. Provide LED lamp to illuminate bottle filler area during activation.

b. Activation:

Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer. Provide [115-volt, plug-in transformer] [battery power pack].

2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2 N) force to operate air-actuated valve.
c. Spout: Laminar flow spout. Fill rate 1.0 gpm (0.6314 L/s).

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements. Not offered for units with Battery Activation.

d. Bottle Counter Display: Provide LED screen that activates during use to display number of uses that equate to 16-ounce bottles, and water filter status.

1) Provide bottle-filled count that does not reset with change of filter or power interruption.

Retain "Bottle Filler, Vandal Resistant" Subparagraph below for models A171.8-UG-VR-D1-BFS, A172.8-UG-VR-D1-BFS, A171408S-FG-VR-BFS, and A172408S-FG-VR-BFS.

12. Bottle Filler, Vandal Resistant: Accessible vandal-resistant design with coordinated installation for single-station drinking fountain and bi-level accessible station. Drinking fountain basin will serve as drain.

a. Housing: 18-gauge Type 304 stainless steel with exposed surfaces polished to a No. 4 satin finish.

b. Activation:
Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer with [115-volt plug-in transformer] [battery power pack].

2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2 N) force to operate air-actuated valve.
c. Spout: Laminar Flow Spout. Fill rate 1.0 gpm (0.6314 L/s).

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements. Not offered for units with Battery Activation.

d. Bottle Counter Display: Provide LED screen that activates during use to display number of uses that equate to 16-ounce bottles, and water filter status.

1) Provide bottle-filled count that does not reset with change of filter or power interruption.

13. Drain: Grid with 1-1/4-inch (32 mm) OD tailpiece.

14. Supply: NPS 3/8 (DN 10) with shutoff valve.

15. Waste Fitting: ASME A112.18.2/CSA B125.2, 1-1/4-inch (32 mm) OD, brass P-trap.

16. Filtration:
Retain one of the two subparagraphs below when required. “EZ Door” is a brand name of Murdock Manufacturing, and is offered as an option for A17 Series units only, with the exception of -SO, -SOC, and -FG models.
a. Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)] effective lifespan.
b. Provide [EZ Door] filter assembly with lockable cover, allowing access beneath skirt for replacement with lead, chlorine, and cyst reduction filter rated for 1500 gal (6800 L) effective lifespan. Furnish key for each unit having lockable cover furnished for Project.
17. Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

b. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

18. Capacities and Characteristics:

a. Cooled Water: [8 gph (30 L/h)] <Insert value>.

b. Ambient-Air Temperature: 90 deg F (32 deg C).

c. Inlet-Water Temperature: 80 deg F (27 deg C).

d. Cooled-Water Temperature: 50 deg F (10 deg C).

e. Electrical Characteristics:

1) Motor Horsepower: [1/5] <Insert value>.

2) Volts: 120-V ac.

3) Phase: Single.

4) Hertz: 60.

5) Full-Load Amperes: [5] <Insert value>.

f. Provide insulation on cooled water lines.

19. Ventilation Grille: Stainless steel.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements.  Verify available options with basis-of-design manufacturer's standard selections.

20. Accessories:

a. Back panel splash plate.

b. Cane skirt kit for upper unit on bi-level fountains.

c. Concealed support carrier.
Coordinate "Drop-down filter access door" Subparagraph below with "Filtration" Subparagraph above.
d. Drop-down filter access door.

Coordinate "Support" Subparagraph below with "Supports" Article.

21. Support: Standard wall-mounting bracket for attaching to substrate.

22. Water Cooler Mounting Height: [Standard] [Child] [Handicapped/elderly, in accordance with ICC A117.1].

C. Drinking Fountains: Stainless steel pressure water coolers, wall mounted, with trim panel <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

A131.8-VR Series, refrigerated, barrier-free, vandal-resistant, wall-mounted drinking fountain.
A131.8-VR-BF Series, refrigerated, barrier-free, vandal-resistant, wall-mounted drinking fountain with semi-recessed bottle filler.

A132.8-VR Series, refrigerated, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with 32-inch panel.

A132.8-VR-BF Series, refrigerated, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with semi-recessed bottle filler.

A151.8-FG Series, refrigerated, barrier-free, 14 gauge stainless steel, wall-mounted drinking fountain.

A151.8-FG-BF Series, refrigerated, barrier-free, 14 gauge stainless steel, wall-mounted drinking fountain with semi-recessed bottle filler.

A151.8-VR Series, refrigerated, barrier-free, vandal-resistant, wall-mounted drinking fountain.

A151.8-VR-BF Series, refrigerated, barrier-free, vandal-resistant, wall-mounted drinking fountain with semi-recessed bottle filler.

A152.8-FG Series, refrigerated, barrier-free, bi-level, wall-mounted 14 gauge stainless steel drinking fountain with 32-inch trim panel.

A152.8-FG-BF Series, refrigerated, barrier-free, bi-level, wall-mounted, 14 gauge stainless steel drinking fountain with semi-recessed bottle filler and 32-inch trim panel.

A152.8-VR Series, refrigerated, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with 32-inch trim panel.

A152.8-VR-BF Series, refrigerated, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with semi-recessed bottle filler and 32-inch trim panel.

1. Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A131.8-VR] [A131.8-VR-BF] [A132.8-VR] [A132.8-VR-BF] [A151.8-FG] [A151.8-FG-BF] [A151.8-VR] [A151.8-VR-BF] [A152.8-FG] [A152.8-FG-BF] [A152.8-VR] [A152.8-VR-BF] or comparable product by one of the following:
a. Elkay Manufacturing Co.

b. Oasis International.

c. <Insert manufacturer's name>.
2. Standards:

a. Comply with:

1) ASHRAE 15, or where applicable, ASHRAE 34.

2) ASME A112.18.1/CSA B125.

3) IAPMO IGC 226.

Retain first subparagraph below for wheelchair-accessible, wall-mounted, pressure water cooler.

4) ICC A117.1.
5) NSF 61 and NSF 372.

6) UL 399 and CSA C22.2, No. 120.

7) Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC).

3. Receptor: Type 304 stainless steel, No. 4, satin finish.
4. Back Panel: Stainless steel wall plate behind drinking fountain with No. 4 satin finish

5. Bubbler: [One] [Two] [flexible with gray finish] [lead-free stainless steel], with anti-rotation, non-squirt design.

6. Maximum Water Flow: 0.5 gpm (1.9 L/m).

7. Cabinet: [Single] [Bi-level cabinets] [Bi-level cabinets with bi‑level skirt kit].
Retain "Accessible Drinking Fountain Orientation" Subparagraph below only for A132 series and A152 series bi-level models.

8. Accessible Drinking Fountain Orientation: On [left] [right] side, when facing unit.

Retain "Control, Push Button" or "Control, Sensor Operated Subparagraph below.

Retain "Control, Push Button” Subparagraph for models A131.8-VR, A131.8-VR-BF, A132.8-VR, A132.8-VR-BF, A151.8-FG, A151.8-FG-BF, A151.8-VR-BF, A151.8-VR, A152.8-FG, A152.8-FG-BF, A152.8-VR, and A152.8-VR-BF.
9. Control, Push Button: Round, vandal-resistant push-button operated cartridge-style valve, having front access adjustable stream regulator.
Retain "Control, Sensor-Operated" Subparagraph below for models having "SO" suffix.
10. Control, Sensor Operated: Infrared sensor-operated valve, preset for maximum 20 second run time.

a. Sensor Location: [Front apron] [Undermount concealed].
b. Flow Restrictor: 0.5 gpm (1.9 L/m).

c. Valve: 9 V dc electronic solenoid valve.
11. Drain: Grid with 1-1/4-inch (32 mm) OD tailpiece.

12. Supply: NPS 1/2 (DN 15) with shutoff valve.

13. Waste Fitting: ASME A112.18.2/CSA B125.2, 1-1/4-inch (32 mm) OD, brass P-trap.

Retain "Bottle Filler, Accessible, Vandal Resistant" Subparagraph below for models A171.8-UG-BF, A172.8-UG-BF, A171.8-UG-VR-BF, A172.8-UG-VR-BF, A191.8, A191.8-BF, A192.8, and A192.8-BF.

14. Bottle Filler, Accessible, Vandal Resistant: Accessible, vandal-resistant design integrated into trim panel for single-station drinking fountain and bi-level accessible station.

a. Activation:

Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer. Provide 115-volt, plug-in transformer.
2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2N) force to operate air-actuated valve.
b. Spout: Laminar flow spout. Fill rate 1.0 gpm (3.8 L/m).
Retain "Filtration" Subparagraph below only if required.

c. Filtration: Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)] effective lifespan.

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements. Not offered for units with Battery Activation.

d. Bottle Counter Display: Provide LED screen that activates during use to display number of uses that equate to 16-ounce bottles, and water filter status.

1) Provide bottle-filled count that does not reset with change of filter or power interruption.

Accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.
15. Accessories:

a. Filter access panel for bi-level units.

b. Back panel splash plate.

c. Cane skirt kit for upper unit for bi-level fountains.

d. High polish stainless steel.
16. Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

b. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

17. Capacities and Characteristics:

a. Cooled Water: [8 gph (30 L/h)] <Insert value>.

b. Ambient-Air Temperature: 90 deg F (32 deg C).

c. Inlet-Water Temperature: 80 deg F (27 deg C).

d. Cooled-Water Temperature: 50 deg F (10 deg C).

e. Electrical Characteristics:

1) Motor Horsepower: [1/5] <Insert value>.

2) Compressor: [115 V, 60 Hz, 4.6 A] [220 V, 50 Hz, 2.5 A].
3) Phase: Single.

f. Provide insulation on cooled water lines.
18. Ventilation Grille: Stainless steel.

19. Support: In-wall mounting frame to receive fixture trim plate.

Coordinate "Support" Subparagraph below with "Supports" Article.

20. Support: Standard wall-mounting bracket for attaching to substrate.
21. Water Cooler Mounting Height: [Standard] [Child] [Handicapped/elderly, in accordance with ICC A117.1].

Copy "Bottle Filling Station with Pressured Water Cooler" Paragraph below and re-edit for each type of in-wall mounted bottle filling station required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each bottle filling station.

D. Bottle Filling Station with Pressure Water Cooler<Insert drawing designation>: wall mounted[, standard][, wheelchair accessible][, vandal resistant].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed. 
BF38 Series, refrigerated, semi-recessed, push-button operated bottle filler.
BF48 Series, refrigerated, semi-recessed, sensor-operated bottle filler.
BF158 Series, refrigerated, surface mount push-button operated bottle filler.
BF168 Series, refrigerated, surface mount sensor-operated bottle filler.
BFEZ168 Series, compact, refrigerated, wall mounted, sensor operated, refrigerated bottle filler.

BFEZ268 Series, compact, refrigerated, wall-mounted universal bi-level, sensor-operated, refrigerated bottle filler.
A1711080-BF2S, refrigerated, vandal-resistant, wall-mounted, sensor-operated bottle filler.
1. Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [BF38] [BF48] [BF158] [BF168] [BFEZ168] [BFEZ268] [A1711080-BF2S] <Insert product name or designation> or comparable product by one of the following:
a. Elkay Manufacturing Co.

b. Oasis International.

c. <Insert manufacturer's name>.
2. Standards:

a. Comply with:
1) ASHRAE 15, or where applicable, ASHRAE 34.

2) ASME A112.18.1/CSA B125.

3) IAPMO IGC 226.

Retain first subparagraph below for wheelchair-accessible, wall-mounted, pressure water cooler.

4) ICC A117.1, CSA B651.

5) NSF 61 and NSF 372.

6) UL 399 and CSA C22.2, No. 120.

7) Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC).

3. Cabinet: [Stainless steel] [Powder coated steel with stainless steel top] <Insert material>.

Retain "Bottle Filler" Subparagraph below when models BF158, BF168, BFEZ168, or BFEZ268 are selected.
4. Bottle Filler: Accessible contour design for coordinated installation with single-station drinking fountain and bi-level accessible station.

a. Housing: Minimum 20-gauge, Type 304 stainless steel with exposed surfaces polished to No. 4 satin finish with contour to align with drinking fountain basin.
1) Fabricate bottle filler area of antimicrobial, impact-resistant, ABS plastic.

2) Provide LED light that illuminates during bottle fill activation.

b. Activation:

Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer. Provide [115-volt, plug-in transformer] [battery power pack].

2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2 N) force to operate air-actuated valve.

c. Spout: Laminar flow spout. Fill rate 1.0 gpm (3.8 L/m).

Retain "Filtration" Subparagraph below only if required.

d. Filtration: Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)] effective lifespan.

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements. Not offered for units with Battery Activation.
e. Bottle Counter Display: Provide LED screen that activates during use to display number of uses that equate to 16-ounce bottles, and water filter status.

1) Provide bottle-filled count that does not reset with change of filter or power interruption.

Retain "Bottle Filler, Vandal Resistant" Subparagraph below when model A1711080-BF2S is selected.
5. Bottle Filler, Vandal Resistant: Drinking fountain receptor serves as bottle filler drain.

a. Housing: Minimum 18-gauge, Type 304 stainless steel with exposed surfaces polished to No. 4 satin finish with contour to align with drinking fountain basin.

b. Activation:

Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer. Provide [115-volt, plug-in transformer] [battery power pack].

2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2 N) force to operate air-actuated valve.

c. Spout: Laminar flow spout. Fill rate 1.0 gpm (3.8 L/m).

Retain "Filtration" Subparagraph below only if required.

d. Filtration: Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)] effective lifespan.

Retain "Bottle Filler" Subparagraph below when models BF38 or BF48 are selected.

6. Bottle Filler: Accessible, vandal-resistant, semi-recessed design.

a. Activation:

Retain one of first two subparagraphs below as required to suit Project requirements.

1) 9-volt infrared sensor, preset with 20-second automatic shut-off timer. Provide [115-volt, plug-in transformer] [battery power pack].

2) Pneumatic hemispherical push button requiring less than 5 pounds (22.2 N) force to operate air-actuated valve.

b. Spout: Laminar flow spout. Fill rate 1.0 gpm (3.8 L/m).
c. Drain: Type304 stainless steel screen.
Retain "Filtration" Subparagraph below only if required.

d. Filtration: Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)] effective lifespan.

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements. Not offered for units with Battery Activation.
e. Bottle Counter Display: Provide LED screen that activates during use to display number of uses that equate to 16-ounce bottles, and water filter status.

1) Provide bottle-filled count that does not reset with change of filter or power interruption.

7. Drain: Grid with 1-1/4-inch (32 mm) OD tailpiece.

8. Supply: NPS 3/8 (DN 10) with shutoff valve.

9. Waste Fitting: ASME A112.18.2/CSA B125.2, 1-1/4-inch (32 mm) OD, brass P-trap.

If cooling is not required, see Section 224713 "Drinking Fountains" for selection.

10. Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

b. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

11. Capacities and Characteristics:

a. Cooled Water: [8 gph (30 L/h)] <Insert value>.

b. Ambient-Air Temperature: 90 deg F (32 deg C).

c. Inlet-Water Temperature: 80 deg F (27 deg C).

d. Cooled-Water Temperature: 50 deg F (10 deg C).

e. Electrical Characteristics:

1) Motor Horsepower: [1/5] <Insert value>.

2) Compressor: [115 V, 60 Hz, 4.6 A] [220 V, 50 Hz, 2.5 A].

3) Phase: Single.

In "Full Load Amps" Subparagraph below, retain first option for units with 115 V, 60 Hz power source. Retain second option for units with 220 V, 50 Hz power source.
4) Full Load Amps: [4.6 A] [2.5 A].

f. Provide insulation on cooled water lines.
12. Ventilation Grille: Stainless steel.

13. Support:
Retain first subparagraph below if models BF158, BF168, BFEZ168, BFEZ268, or A1711080-BF2S are selected.

a. Fixture mounting plate with brackets for attaching to wood blocking or substrate

Retain first subparagraph below if models BF38 or BF48 are selected.

b. In-wall mounting frame to receive fixture trim plate.
Retain subparagraph below if models BFEZ168, BFEZ268, or A1714080-BF2S are selected.

c. Concealed in-wall support carrier.
14. Bottle Filling Station Mounting Height: [Standard] [Child] [Handicapped/elderly in accordance with ICC A117.1].

E. Drinking Fountains: Stainless steel, recessed, pressure water coolers, <Insert drawing designation>: [cuspidor] [, wheelchair accessible] [, bottle filler].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AI81.8 Series, refrigerated, barrier-free, fully recessed, wall-mounted drinking fountain.
AL81.8-BF Series, refrigerated, fully recessed, wall-mounted drinking fountain with bottle filler.
AR81.8-BF Series, refrigerated, fully recessed, barrier-free, wall-mounted drinking fountain with bottle filler.
A481.8 Series, refrigerated, fully recessed, wall-mounted drinking fountain.
A481.8CUSP Series, refrigerated, fully recessed, wall-mounted drinking fountain and cuspidor.
1. Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [AI81.8] [A481.8] [A481.8CUSP] [AL81.8-BF] [AR81.8-BF] or comparable product by one of the following:

a. Elkay Manufacturing Co.
b. Oasis International.

c. <Insert manufacturer's name>.
2. Standards:

a. Comply with:

1) ASHRAE 15, or where applicable, ASHRAE 34.

2) ASME A112.19.2/CSA B145.1.

3) NSF 61 and NSF 372.
Retain first subparagraph below for wheelchair-accessible, wall-mounted, pressure water cooler.

4) ICC A117.1.
3. Receptor Shape: Concave with flush wall flange.

4. Drinking Fountain Bubbler: One [flexible bubbler with gray finish,] [stainless steel bubbler,] located on deck, anti-rotation, non-squirt design.

5. Drinking Fountain Control: Push-button operated cartridge-style valve, having front access adjustable stream regulator.

Retain "Bottle Filler" Subparagraph below if models AL81408S or AR81408S are selected, and bottle filler is included in Project design.

6. Bottle Filler: Provide ligature resistant bottle and cup filler, located in back wall.

7. Maximum Water Flow: 0.5 gpm (1.9 L/m).

Retain "Cuspidor" Subparagraph below if model A481.8CUSP is selected.

8. Cuspidor: Provide additional receptor with stainless steel wash down outlet in lieu of drinking bubbler.

9. Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

10. Drain: Grid with 1-1/4 inch (32 mm) OD, minimum, horizontal waste and trap, complying with ASME A112.18.2/CSA B125.2.

Retain "Filtration" Subparagraph below only if required.

11. Filtration: Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L] [3000 gal (13600 L)] effective lifespan.

12. Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

b. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

13. Capacities and Characteristics:

a. Cooled Water: [8 gph (30 L/h)] <Insert value>.

b. Ambient-Air Temperature: 90 deg F (32 deg C).

c. Inlet-Water Temperature: 80 deg F (27 deg C).

d. Cooled-Water Temperature: 50 deg F (10 deg C).

e. Electrical Characteristics:

1) Motor Horsepower: [1/5] <Insert value>.

2) Compressor: [115 V, 60 Hz, 4.6 A] [220 V, 50 Hz, 2.5 A].

3) Phase: Single.

In "Full Load Amps" Subparagraph below, retain first option for units with 115 V, 60 Hz power source. Retain second option for units with 220 V, 50 Hz power source.

4) Full Load Amps: [4.6 A] [2.5 A].

f. Provide insulation on cooled water lines.

14. Ventilation Grille: Stainless steel [with ligature resistant design]. Locate grille and chiller [below unit] [above unit].

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements.

15. Accessories:

a. Glass filler.

b. High polish stainless steel.

c. Less drinking bubbler and push button.

16. Support: Mounting frame or brackets for attaching to wood blocking or substrate.

2.2 SUPPORTS

A. Type I Water Cooler Carrier:
Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Jay R. Smith Mfg Co; a division of Morris Group International.

b. Josam Company.

c. <Insert manufacturer's name>.
2. Standard: ASME A112.6.1M.

B. Type II Water Cooler Carrier:
Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Jay R. Smith Mfg Co; a division of Morris Group International.

b. Josam Company.

c. <Insert manufacturer's name>.

2. Standard: ASME A112.6.1M.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for water-supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before fixture installation.

B. Examine walls and floors for suitable conditions where fixtures will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install fixtures level and plumb in accordance with roughing-in drawings. For fixtures indicated for children, install at height required by authorities having jurisdiction.

B. Set freestanding pressure water coolers on floor.

C. Install off-the-floor carrier supports, affixed to building substrate, for wall-mounted fixtures.

D. Install mounting frames, affixed to building construction, and attach recessed, pressure water coolers, and in-wall bottle filling stations to mounting frames.

E. Install water-supply piping with shutoff valve on supply to each fixture to be connected to domestic-water distribution piping. Use ball or gate valve. Install valves in locations where they can be easily reached for operation. Valves are specified in Section 220523.12 "Ball Valves for Plumbing Piping" and Section 220523.15 "Gate Valves for Plumbing Piping."

F. Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.

G. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons where required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

H. Seal joints between fixtures and walls using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

B. Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

C. Install ball or gate shutoff valve on water supply to each fixture.[ Install valve upstream from filter for water cooler.] Comply with valve requirements specified in Section 220523.12 "Ball Valves for Plumbing Piping" and Section 220523.15 "Gate Valves for Plumbing Piping."

D. Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

3.4 ADJUSTING

A. Adjust fixture flow regulators for proper flow and stream height.

B. Adjust pressure water-cooler temperature settings.

3.5 CLEANING

A. After installing fixture, inspect unit. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.

B. Clean fixtures, on completion of installation, in accordance with manufacturer's written instructions.

C. Provide protective covering for installed fixtures.

D. Do not allow use of fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224716
	PRESSURE WATER COOLERS
	224716 - 1



