Copyright 2018 AIA
MasterSpec Full Length
09/18 (PM 12/22)
PRODUCT MASTERSPEC LICENSED BY DELTEK, INC. TO WHITEHALL MANUFACTURING; MORRIS GROUP INTERNATIONAL

Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Whitehall Manufacturing; Morris Group International ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Whitehall Manufacturing; Morris Group International, P.O. Box 3527, City of Industry, CA 91744-0527; Phone: (626) 968-6681; Fax: (626) 855-4862; Website: https://www.whitehallmfg.com/home; Email: <Insert email address>.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 221319.13 - SANITARY DRAINS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>
Revise this Section by deleting and inserting text to meet Project-specific requirements.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Ligature-resistant drain strainers.

2. Floor drains.

3. Floor sinks.

4. Trench drains.

5. Channel drainage systems.

1.2 DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.
A. ABS: Acrylonitrile-butadiene styrene.

B. FRP: Fiberglass-reinforced plastic.

C. HDPE: High-density polyethylene.

D. PE: Polyethylene.

E. PP: Polypropylene.

F. PVC: Polyvinyl chloride.

1.3 ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

A. Product Data: For each type of product.

PART 2 -  PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."
Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

2.1 DRAIN ASSEMBLIES

A. Provide sanitary drains bearing label, stamp, or other markings of specified testing agency.

B. Comply with NSF 14 for plastic sanitary piping specialty components.

2.2 LIGATURE-RESISTANT DRAIN STRAINERS
Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product. 

A. Ligature-Resistant Shower Drain Strainers <Insert drawing designation if any>:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require products from Whitehall Manufacturing; Morris Group International, BestCare Series or comparable product from manufacturers listed.

Retain first option for shower drain with ligature-resistant strainer-WHPG Series, designed for use on Oatey 42150 drain body only.

Retain second option for ligature-resistant, no-caulk shower drain with strainer, WHPD-2NH Series, for installation with preformed shower stall bases.

1. Basis-of-Design Product: Subject to compliance with requirements, provide Whitehall Manufacturing; Morris Group International, BestCare model [WHPG] [WHPD-2NH]; <Insert drawing designation> or comparable product by one of the following:

a. Josam Company.

b. Zurn Industries, LLC.

c. <Insert manufacturer's name>.

2. Material: 16 gauge, Type 304 stainless steel.

3. Top Shape: Round.

4. Dimensions of Top or Strainer: 4.13 inch (105 mm).

5. Body Material: Brass.

6. Shower Drain Strainer Hardware: Manufacturer's standard ligature-resistant hardware required to secure strainer grate to drain body. 

B. Ligature-Resistant Floor Drain Strainers <Insert drawing designation if any>:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require products from Whitehall Manufacturing; Morris Group International, BestCare Series or comparable product from manufacturers listed.

Products listed are suitable for use only with JR Smith floor drains in poured finished floors.

1. Basis-of-Design Product: Subject to compliance with requirements, provide Whitehall Manufacturing; Morris Group International, model [WHDG-5RD] [WHDG-6RD] [WHDG-5SQ] [WHDG-6SQ] [WHDG-5RD-SS] [WHDG-6RD-SS] [WHDG-5SQ-SS] [WHDG-6SQ-SS]; <Insert drawing designation> or comparable product by one of the following:

a. Josam Company.

b. Zurn Industries, LLC. 

c. <Insert manufacturer's name>.

In "Grate Material" Subparagraph below, retain first option for Whitehall Manufacturing; Morris Group International, BestCare Series models WHDG-5RD, WHDG-6RD, WHDG-5SQ, and WHDG-6SQ. Retain second option for models WHDG-5RD-SS, WHDG-6RD-SS, WHDG-5SQ-SS, and WHDG-6SQ-SS.

2. Grate Material: [Nickel bronze] [Stainless steel].
3. Top Shape: [Round] [Square].
4. Grate Dimensions: [5 inch (127 mm)] [6 inch (152 mm)].

5. Floor Drain Strainer Hardware: Manufacturer's standard ligature-resistant hardware required to secure strainer grate to drain body.

2.3 FLOOR DRAINS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Cast-Iron Floor Drains <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Commercial Enameling Company.

b. Jay R. Smith Mfg Co; a division of Morris Group International.

c. Josam Company.

d. MIFAB, Inc.

e. Prier Products, Inc.

f. Sioux Chief Manufacturing Company, Inc.

g. Wade; a subsidiary of McWane Inc.

h. WATTS.

i. Zurn Industries, LLC.

j. <Insert manufacturer's name>.

2. Standard: ASME A112.6.3[ with backwater valve].

3. Pattern: [Area] [Floor] [Funnel floor] [Sanitary] <Insert pattern> drain.

4. Body Material: [Gray iron] <Insert material>.

Retain one or more of 17 subparagraphs below to suit Project design.

5. Seepage flange.

6. Anchor flange.

7. Clamping device.

8. Outlet: [Bottom] [Side] <Insert type>.

9. Backwater Valve: [Drain-outlet type] [Integral, ASME A112.14.1, swing-check type].

Coating in "Coating on Interior and Exposed Exterior Surfaces" Subparagraph below is usually used only on sanitary floor drains.

10. Coating on Interior and Exposed Exterior Surfaces: [Acid-resistant enamel] <Insert material>.

11. Sediment Bucket: <Insert description>.

12. Top or Strainer Material: [Bronze] [Gray iron] [Nickel bronze] [Stainless steel] <Insert material>.

13. Top of Body and Strainer Finish: [Nickel bronze] [Polished bronze] [Rough bronze] [Stainless steel] <Insert finish>.

14. Top Shape: [Round] [Square] <Insert shape>.

15. Dimensions of Top or Strainer: <Insert dimensions and describe body, sump, and grate>.

16. Top Loading Classification: [Extra Heavy Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

17. Funnel: <Insert description and dimensions>.

18. Inlet Fitting: [Gray iron, with threaded inlet and threaded or spigot outlet, and trap-seal primer valve connection].

19. Trap Material: [Bronze] [Cast iron] [Copper] <Insert material>.

20. Trap Pattern: [Deep-seal P-trap] [Standard P-trap] <Insert pattern>.

21. Trap Features: [Cleanout] [Trap-seal primer valve drain connection] [Cleanout and trap-seal primer valve drain connection] <Insert type>.

B. Ligature-Resistant Cast-Iron Floor Drains <Insert drawing designation>:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require products from Whitehall Manufacturing; Morris Group International, BestCare Series or comparable product from manufacturers listed.

Whitehall models WHFD and WHFD-SS are intended for drain applications in concrete or ceramic tile floors. Models WHFDV and WHFDV-SS are intended for drain applications in floors with vinyl or other resilient floor covering.
Retain model WHFDV-6RD-2NH for floor drain with ligature-resistant strainer in vinyl finished floors.
1. Basis-of-Design Product: Subject to compliance with requirements, provide Whitehall Manufacturing; Morris Group International model [WHFD-5RD-2NH] [WHFD-6RD-2NH] [WHFD-5SQ-2NH] [WHFD-6SQ-2NH] [WHFD-5RD-2NH-SS] [WHFD-6RD-2NH-SS] [WHFD-5SQ-2NH-SS] [WHFD-6SQ-2NH-SS] [WHFDV-6RD-2NH] Series; <Insert drawing designation> or comparable product by one of the following:

a. Josam Company.

b. Zurn Industries, LLC.

c. <Insert manufacturer's name>.

2. Standard: ASME A112.6.3[ with backwater valve].

3. Body Material: Cast iron.
Retain one or more of first three subparagraphs below to suit Project design.

4. Seepage flange.

5. Anchor flange.

6. Clamping device.

In "Grate Material and Finish" Subparagraph below, retain first option for models WHFD-5RD-2NH, WHFD-6RD-2NH, WHFD-5SQ-2NH, WHFD-6SQ-2NH, and WHFDV-6RD-2NH. Retain second option for models WHFD-5RD-2NH-SS, WHFD-6RD-2NH-SS, WHFD-5SQ-2NH-SS, and WHFD-6SQ-2NH-SS.

7. Grate Material and Finish: [Nickel bronze] [Stainless steel].

8. Grate Shape: [Round] [Square].

9. Grate Dimension: [5 inch (127 mm)] [6 inch (152 mm)].

10. Ligature-Resistant Cast Iron Floor Drain Hardware: Manufacturer's standard ligature-resistant hardware required to secure strainer grate to drain body.

C. Stainless Steel Floor Drains, ASME A112.3.1 <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Zurn Industries, LLC.

b. <Insert manufacturer's name>.

2. Outlet: [Bottom] [Side] <Insert type>.

3. Top or Strainer Material: [Stainless steel] <Insert material>.

4. Top Shape: [Round] [Square] <Insert shape>.

5. Dimensions of Top or Strainer: <Insert dimensions and describe body, sump, and grate>.

Retain one or more of six subparagraphs below to suit Project design.

6. Seepage flange.

7. Anchor flange.

8. Clamping device.

9. Trap-primer connection.

10. Trap Material: [Cast iron] [Stainless steel] <Insert material>.

11. Trap Pattern: [Deep-seal P-trap] [Standard P-trap] <Insert pattern>.

D. Stainless Steel Floor Drains, ASME A112.6.3 <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. BLÜCHER; A Watts brand.

b. Jay R. Smith Mfg Co; a division of Morris Group International.

c. Josam Company.

d. Kusel Equipment Co.

e. Scherping Systems, Inc.

f. Sioux Chief Manufacturing Company, Inc.

g. Wade; a subsidiary of McWane Inc.

h. WATTS.

i. Zurn Industries, LLC.

j. <Insert manufacturer's name>.

2. Outlet: [Bottom] [Side] <Insert type>.

3. Top or Strainer Material: [Stainless steel] <Insert material>.

4. Top Shape: [Round] [Square] <Insert shape>.

5. Dimensions of Top or Strainer: <Insert dimensions and describe body, sump, and grate>.

Retain one or more of six subparagraphs below to suit Project design.

6. Seepage flange.

7. Anchor flange.

8. Clamping device.

9. Trap-primer connection.

10. Trap Material: [Cast iron] [Stainless steel] <Insert material>.

11. Trap Pattern: [Deep-seal P-trap] [Standard P-trap] <Insert pattern>.

E. Ligature-Resistant Linear Drains <Insert drawing designation>:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require products from Whitehall Manufacturing; Morris Group International, BestCare Series or comparable product from manufacturers listed.

Ligature-resistant linear drain with flashing flange: WHLD Series.
1. Basis-of-Design Product: Subject to compliance with requirements, provide Whitehall Manufacturing; Morris Group International; BestCare model [WHLD-12-F] [WHLD-24-F] [WHLD-36-F] [WHLD-48-F] [WHLD-60-F] or comparable product by one of the following:

a. Josam Company.

b. Zurn Industries, LLC.

c. <Insert manufacturer's name>.

2. Outlet: Bottom.

3. Top or Strainer Material: Type 304 stainless steel polished to a No. 4 satin finish.

4. Top Shape: Rectangular.

5. Dimensions of Top or Strainer: 2.25 inch (57 mm) width x [12 inch (305 mm)] [24 inch (610 mm)] [36 inch (915 mm)] [48 inch (1220 mm)] [60 inch (1525 mm)] length.

Retain one or more of first two subparagraphs below to suit Project design.

6. Flashing flange.

7. Clamping device.

8. Drain Body Material: Type 304 stainless steel.

F. Plastic Floor Drains <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. Josam Company.

d. Oatey.

e. Plastic Oddities.

f. Sioux Chief Manufacturing Company, Inc.

g. Zurn Industries, LLC.

h. <Insert manufacturer's name>.

2. Standard: ASME A112.6.3.

3. Material: [ABS] [or] [PVC] <Insert material>.

Retain one or more of first six subparagraphs below to suit Project design.

4. Seepage flange.

5. Clamping device.

6. Outlet: [Bottom] [Side] <Insert type>.

7. Sediment Bucket: <Insert description>.

8. Top or Strainer Material: [Bronze] [Plastic] [Stainless steel] <Insert other>.

9. Top of Body and Strainer Finish: [Nickel bronze] [Polished bronze] [Rough bronze] [Stainless steel] <Insert other>.

10. Top Shape: [Round] [Square] <Insert shape>.

11. Dimensions of Top or Strainer: <Insert dimensions and describe body, sump, and grate if required>.

12. Trap Material: [Cast iron] [Plastic drainage piping] <Insert material>.

13. Trap Pattern: [Standard P-trap] <Insert pattern>.

2.4 FLOOR SINKS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Cast-Iron Floor Sinks <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Commercial Enameling Company.

b. Jay R. Smith Mfg Co; a division of Morris Group International.

c. Josam Company.

d. Wade; a subsidiary of McWane Inc.

e. WATTS.

f. Zurn Industries, LLC.

g. <Insert manufacturer's name>.

2. Standard: ASME A112.6.7.

3. Pattern: [Floor] [Funnel floor] <Insert pattern> drain.

4. Body Material: Cast iron.

Retain one or more of 14 subparagraphs below to suit Project design.

5. Anchor Flange: [Not required] [Required] [, with seepage holes].

6. Clamping Device: [Not required] [Required].

7. Outlet: Bottom, [no-hub] <Insert type> connection.

8. Coating on Interior Surfaces: [Not required] [Acid-resistant enamel] <Insert coating>.

9. Sediment Bucket: [Not required] <Insert description>.

10. Internal Strainer: [Not required] [Dome] [Flat].

11. Internal Strainer Material: [Aluminum] <Insert material>.

12. Top Grate Material: [Cast iron] <Insert material>[, loose] [, hinged].

13. Top of Body and Grate Finish: [Nickel bronze] [Acid-resistant enamel] <Insert finish>.

14. Top Shape: [Round] [Square] <Insert shape>.

15. Dimensions of Top Grate: <Insert dimensions and describe grate pattern>.

16. Top Loading Classification: [No traffic] <Insert traffic loading>.

17. Funnel: [Not required] [Required]. <Insert material, shape, and dimensions>.

18. <Insert additional options here>.

B. Stainless Steel Floor Sinks, ASME A112.6.7 <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Jay R. Smith Mfg Co; a division of Morris Group International.

b. Josam Company.

c. Wade; a subsidiary of McWane Inc.

d. WATTS.

e. Zurn Industries, LLC.

f. <Insert manufacturer's name>.

2. Standard: ASME A112.6.7.

3. Pattern: [Floor] [Funnel floor] <Insert pattern> drain.

4. Body Material: Stainless steel.

Retain one or more of 13 subparagraphs below to suit Project design.

5. Anchor flange[ with seepage holes].

6. Clamping device.

7. Outlet: Bottom, [no-hub] <Insert type> connection.

8. Sediment Bucket: <Insert description>.

9. Internal Strainer: [Dome] [Flat].

10. Internal Strainer Material: [Stainless steel] <Insert material>.

11. Top Grate Material: [Stainless steel] <Insert material>[, loose][, hinged].

12. Top of Body and Grate Finish: [Satin nickel] [Stainless steel] <Insert finish>.

13. Top Shape: [Round] [Square] <Insert shape>.

14. Dimensions of Top Grate: <Insert dimensions and describe grate pattern>.

15. Top Loading Classification: [No traffic] <Insert traffic loading>.

16. Funnel: <Insert material, shape and dimensions>.

17. <Insert additional options here>.

C. Plastic Floor Sinks <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. Oatey.

d. Plastic Oddities.

e. <Insert manufacturer's name>.

2. Standard: ASME A112.6.7.

3. Pattern: [Floor] [Funnel floor] <Insert pattern> drain.

4. Body Material: PVC.

5. Outlet: Bottom, PVC primer and solvent cement connection.

Retain one or more of nine subparagraphs below to suit the Project design.

6. Sediment Bucket: <Insert description>.

7. Internal Strainer: [Dome] [Flat].

8. Internal Strainer Material: [PVC] <Insert material>.

9. Top Grate Material: [PVC] <Insert material>.

10. Top Shape: [Round] [Square] <Insert shape>.

11. Dimensions of Top Grate: <Insert dimensions and describe grate pattern>.

12. Top Loading Classification: [No traffic] <Insert traffic loading>.

13. Funnel: <Insert material, shape and dimensions>.

14. <Insert additional options here>.

2.5 TRENCH DRAINS

Copy paragraph below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Trench Drains <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Jay R. Smith Mfg Co; a division of Morris Group International.

b. Josam Company.

c. MIFAB, Inc.

d. Sioux Chief Manufacturing Company, Inc.

e. Wade; a subsidiary of McWane Inc.

f. WATTS.

g. Zurn Industries, LLC.

h. <Insert manufacturer's name>.

2. Standard: ASME A112.6.3 for trench drains.

3. Material: Ductile or gray iron.

Retain one or more of nine subparagraphs below to suit Project design.

4. Flange: [Anchor] [Seepage] [Not required].

5. Clamping Device: [Not required] [Required].

6. Outlet: [Bottom] [End] [Side] <Insert location>.

7. Grate Material: [Ductile iron] [Ductile iron or gray iron] [Gray iron] [Stainless steel] <Insert material>.

8. Grate Finish: [Painted] [Not required] <Insert finish>.

9. Dimensions of Frame and Grate: <Insert dimensions and describe body, sump, and grate if required>.

10. Top Loading Classification: [Extra Heavy Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

11. Trap Material: [Cast iron] [Stainless steel] [Not required] <Insert material>.

12. Trap Pattern: [Standard P-trap] [Not required] <Insert pattern>.

2.6 CHANNEL DRAINAGE SYSTEMS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Stainless Steel Channel Drainage Systems, ASME A112.3.1 <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by the following:

a. Josam Company.

b. <Insert manufacturer's name>.

2. Description: Modular system of stainless steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Standard: ASME A112.3.1 for trench drains.

4. Channel Sections: Interlocking joint, stainless steel with level invert.

a. Dimensions: [5.8 inches (147 mm)] [11.7 inches (297mm)] wide. Include number of units required to form total lengths indicated.

5. Grates: Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

a. Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

6. Covers: Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

7. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

8. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

B. Stainless Steel Channel Drainage Systems, Non-ASME A112.3.1 <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. MultiDrain Systems, Inc.

b. Zurn Industries, LLC.

c. <Insert manufacturer's name>.

2. Description: Modular system of stainless steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Interlocking joint, stainless steel with level invert.

a. Dimensions: [6 inches (152 mm)] [12 inches (305 mm)] wide. Include number of units required to form total lengths indicated.

4. Grates: Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

a. Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

5. Covers: Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

6. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

7. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

C. Narrow, Sloped-Invert, Polymer-Concrete Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ABT, Inc.

b. ACO USA.

c. Forté Composites, Inc.

d. Hubbell Incorporated (Hubbell Power Systems).

e. Jay R. Smith Mfg Co; a division of Morris Group International.

f. Josam Company.

g. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Narrow, interlocking-joint, sloped-invert, polymer-concrete modular units with end caps.

a. Include rounded bottom, with built-in invert slope of 0.6 percent and with outlets in number, sizes, and locations indicated.

b. Include extension sections necessary for required depth.

c. Dimensions: 4-inch (102-mm) inside width. Include number of units required to form total lengths indicated.

d. Frame: [Gray-iron or galvanized steel for grates] [Not required].

4. Grates: Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

a. Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

1) Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

5. Covers: Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

6. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

7. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

D. Narrow, Level-Invert, Polymer-Concrete Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ABT, Inc.

b. ACO USA.

c. Forté Composites, Inc.

d. Josam Company.

e. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

Indicate locations and lengths of covers on Drawings.

3. Channel Sections: Narrow, interlocking-joint, precast, polymer-concrete modular units with end caps.

a. Include rounded bottom, with level invert and with NPS 4 (DN 100) outlets in number and locations indicated.

b. Dimensions: [5-inch (127-mm)] <Insert dimension> inside width and [9-3/4 inches (248 mm)] <Insert dimension> deep. Include number of units required to form total lengths indicated.

1) Frame: [Gray-iron or galvanized steel for grates] [Not required].

4. Grates: Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

a. Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

5. Covers: Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

6. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

7. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

Indicate locations and lengths of covers on Drawings.

E. Wide, Level-Invert, Polymer-Concrete Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ABT, Inc.

b. ACO USA.

c. Hubbell Incorporated (Hubbell Power Systems).

d. Josam Company.

e. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Wide, interlocking-joint, precast, polymer-concrete modular units with end caps.

a. Include flat or rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

b. Dimensions: [8-inch (203-mm)] <Insert dimension> inside width and [13-3/4 inches (350 mm)] <Insert dimension> deep. Include number of units required to form total lengths indicated.

1) Frame: [Gray-iron or galvanized steel for grates] [Not required].

4. Grates: Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

a. Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

5. Covers: Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

6. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

7. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

F. FRP Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. ACO USA.

b. Aquaduct, Inc.

c. Jay R. Smith Mfg Co; a division of Morris Group International.

d. Zurn Industries, LLC.

e. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Interlocking-joint, sloped-invert, FRP modular units, with end caps. Include flat, rounded, or inclined inside bottom, with outlets in number, sizes, and locations indicated.

a. Dimensions: [4 inches (102 mm)] [4 or 6 inches (102 or 152 mm)] [6 inches (152 mm)] [6 or 8 inches (152 or 203 mm)] [8 inches (203 mm)] wide. Include number of units required to form total lengths indicated.

b. Frame: [Galvanized steel] [Stainless steel] [Manufacturer's standard metal] <Insert material> for grates.

4. Grates: With slots or perforations and widths and thickness that fit recesses in channel sections.

a. Material: [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

5. Covers: Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

6. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

7. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

G. HDPE or PE Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Jay R. Smith Mfg Co; a division of Morris Group International.

b. Sioux Chief Manufacturing Company, Inc.

c. Tuf-Tite Corporation.

d. Zurn Industries, LLC.

e. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Interlocking-joint, HDPE or PE modular units, with end caps. Include flat, rounded, or inclined bottom, with level invert and with outlets in number, sizes, and locations indicated.

a. Dimensions: 4 inches (102 mm) wide. Include number of units required to form total lengths indicated.

4. Grates: With slots or perforations and widths and thickness that fit recesses in channel sections.

a. Material: [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Color: <Insert color or delete subparagraph>.

5. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

6. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

H. PP Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. Infinity Plastics, Inc.

b. Jay R. Smith Mfg Co; a division of Morris Group International.

c. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Interlocking-joint, PP modular units, with end caps. Include flat, rounded, or inclined bottom, with level invert and with outlets in number, sizes, and locations indicated.

a. Dimensions: 4 inches (102 mm) wide. Include number of units required to form total lengths indicated.

4. Grates: With slots or perforations and widths and thickness that fit recesses in channel sections.

a. Material: [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Color: <Insert color or delete subparagraph>.

5. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

6. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

I. PVC Channel Drainage Systems <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

a. MultiDrain Systems, Inc.

b. NDS Inc.

c. <Insert manufacturer's name>.

2. Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

3. Channel Sections: Interlocking-joint, PVC modular units, with end caps. Include flat, rounded, or inclined bottom, with level invert and with outlets in number, sizes, and locations indicated.

a. Dimensions: 4 inches (102 mm) wide. Include number of units required to form total lengths indicated.

4. Grates: With slots or perforations and widths and thickness that fit recesses in channel sections.

a. Material: [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

b. Color: <Insert color or delete subparagraph>.

5. Supports, Anchors, and Setting Devices: Manufacturer's standard, unless otherwise indicated.

6. Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

PART 3 -  EXECUTION

3.1 INSTALLATION

In this article, retain only those sanitary piping specialties that are specified in Part 2. Additional instructions may be required for special applications. Indicate locations of specialties in plans, details, and schematics on Drawings.

A. Install floor drains at low points of surface areas to be drained. Set grates of drains flush with finished floor, unless otherwise indicated.

Coordinate first three subparagraphs below with Drawings.

1. Position floor drains for easy access and maintenance.

2. Set floor drains below elevation of surrounding finished floor to allow floor drainage.

3. Set with grates depressed in accordance with the following drainage area radii:

a. Radius, 30 Inches (750 mm) or Less: Equivalent to 1 percent slope, but not less than 1/4-inch (6.35-mm) total depression.

b. Radius, 30 to 60 Inches (750 to 1500 mm): Equivalent to 1 percent slope.

c. Radius, 60 Inches (1500 mm) or Larger: Equivalent to 1 percent slope, but not greater than 1-inch (25-mm) total depression.

Coordinate first subparagraph below with Drawings.

4. Install floor-drain flashing collar or flange, so no leakage occurs between drain and adjoining flooring.

a. Maintain integrity of waterproof membranes where penetrated.

5. Install individual traps for floor drains connected to sanitary building drain, unless otherwise indicated.

B. Install trench drains at low points of surface areas to be drained.

1. Set grates of drains flush with finished surface, unless otherwise indicated.

Retain first paragraph below if stainless steel channel drains complying with ASME A112.3.1 are required.

C. Comply with ASME A112.3.1 for installation of stainless steel channel drainage systems.

1. Install on support devices, so that top will be flush with adjacent surface.

D. Install FRP channel drainage system components on support devices, so that top will be flush with adjacent surface.

E. Install plastic channel drainage system components on support devices, so that top will be flush with adjacent surface.

F. Install open drain fittings with top of hub [1 inch (25 mm)] [2 inches (51 mm)] <Insert dimension> above floor.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements in Section 221316 "Sanitary Waste and Vent Piping" for piping installation requirements. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Comply with requirements in Section 221319 "Sanitary Waste Piping Specialties" for backwater valves, air admittance devices and miscellaneous sanitary drainage piping specialties.

C. Comply with requirements in Section 221323 "Sanitary Waste Interceptors" for grease interceptors, grease-removal devices, oil interceptors, sand interceptors, and solid interceptors.

D. Install piping adjacent to equipment to allow service and maintenance.

E. Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

F. Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 LABELING AND IDENTIFYING

A. Distinguish among multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations, in addition to identifying unit. Nameplates and signs are specified in Section 220553 "Identification for Plumbing Piping and Equipment."

3.4 PROTECTION

A. Protect drains during remainder of construction period to avoid clogging with dirt or debris and to prevent damage from traffic or construction work.

B. Place plugs in ends of uncompleted piping at end of each day or when work stops.

END OF SECTION 221319.13
	SANITARY DRAINS
	221319.13 - 20



